## Slide 1: Fit for manufacturing (ffm) program Biogen RTP, NC
Adam Tessneer – Quality Technical Services
Alex Lopez – Quality Technical Services
David Davis - Engineering
Dean Mattiace – Facility Operations
Mike Perkins – Manufacturing Tech Ops
Tolga Musa - Manufacturing
ISPE CaSA – 15 February 2021

## Slide 2: Biogen RTP, NC
Overview

## Slide 3
~ONE BILLION PEOPLE
affected by neurological disorders worldwide
Huge impact to the global healthcare system
MULTIPLE
SCLEROSIS
PROGRESSIVE
SUPRANUCLEAR
PALSY
PARKINSON’S
DISEASE
AMYOTROPHIC
LATERAL
SCLEROSIS
SPINAL
MUSCULAR
ATROPHY
DEMENTIA
60-70% HAVE
ALZHEIMER’S
DISEASE
Our MISSION is clear.
We are PIONEERS in neuroscience.

## Slide 4
Biogen RTP Operations

## Slide 5: RTP Bio Site (5000 Davis Dr.) Overview
  Broke ground on NC operations in 1995
  RTP site includes 7 buildings and a central utilities area
  Approximately 1,120 site employees
  Mammalian Cell Derived Therapeutic proteins.
  Commercial and Clinical production
  Batch processing through multiple Bioreactors 60 L – 15,000L
  Batch purification through column chromatography and filtration
  Final facility output is liquid bulk DS which is either frozen or stored at 2-8ᵒ C
  24 x 7 Operations

## Slide 6
RTP Bio Site (5000 Davis Dr.)
B24
B24: 150 kft2
  QC Laboratories
  Stability & Sample Control
  Technical Development
B20
B20: 37 kft2
  Office Space
  Analytical Development
  Manufacturing Sciences
B21
B21: 92 kft2
  Manufacturing: 3 x 2000L
  2 Purification Suites
  Single Use Suite
  Central Utilities
B22
B22: 170 kft2
  Manufacturing: 6 x 15,000L
  3 Seed Trains
  Purification Suite 1
  Clean Utilities
B23
B23: 45 kft2
  Warehouse & Dispensary
B25
B25: 35 kft2
  LSM Purification Suite 2
B26
Central Utilities
B26:208 kft2
  Administration
1996
2001
2002
2003
2012
2015
B22 and B25
  3rd Purification Suite
  3rd Harvest Centrifuge

## Slide 7: RTP Pharma Site Overview
  Original building built in1997 – Additions in 2008 and 2010
  RTP site includes 2 buildings and a central utilities building
  Approximately 300 site employees
  Parenteral Filling – 2 Vial filling lines for commercial/clinical and 1 development line
  Oral Solid Dosage Manufacturing
  Anti-sense Oligonucleotide Manufacturing Suite

## Slide 8
BLDG. 34 – CUB Utility
BLDG. 36 – PF Line 1 and 2 QC Micro
BLDG. 35 – OSM, PF Line 3
RTP Pharma (900 Davis Dr.) Site
BLDG. 35 – Quality Control Labs
Notes: Miles

## Slide 9
Coming Soon: RTP Gene Therapy Manufacturing (GTM)
Gene Therapy Manufacturing Facility

## Slide 10: FIT for Manufacturing program

## Slide 11: Fit for Manufacturing Lifecycle
FFM
Installation
Commissioning
Qualification
Design
System Release
Initial
Fit for Manufacturing
Program Elements
Fit for Manufacturing
A multi-tiered program that includes a series of verifications and control points to ensure system, service or area meets its defined purpose and is fit for GMP manufacturing.

## Slide 12
Governance and Management

## Slide 13
Tiered Readiness Strategy

## Slide 14
FFM Procedure
Equipment “At Use” Inspections
Equipment / System Inspections
Area Inspections
Leadership GEMBAs
Small Parts
Fit for Manufacturing (FFM) Hierarchy
Planned Maintenance Schedules, PM Work Orders, Job Plan Checklists

## Slide 15
Governance
Quarterly Site Management Review (SMR)
Monthly SMR Report
Preventative Maintenance
Corrective Maintenance
Deviations associated with FFM
Inspection Process
Equipment
Equipment Area
Processing Areas
Support Systems
Inspection Escalations
Inspection Matrix
FFM Procedure Outline

## Slide 16: Inspection Matrix
Item | Type | Frequency (Minimum) | Record | Responsibility
Process Equipment | At Use | After Pre-Use | Master Production Record | Manufacturing
 | Periodic | 90 days | Work Order | Manufacturing
 | Periodic (Invasive) | Per Procedure | Work Order | Maintenance
Process Utilities (e.g., CIP Systems) | Periodic | 90 days | Work Order | Engineering
AHU | Periodic | 90 days | Work Order | Maintenance
Clean Utilities | Periodic | 90 days | Work Order | Maintenance
Process Support Systems (e.g., Autoclaves, Parts Washers, COP Baths) | Periodic | 30 days | Work Order | Manufacturing
Small Parts | Periodic | 90 days | Work Order | Manufacturing
Environmental Chambers | Periodic | 90 days | Work Order | Engineering
Unidirectional-Flow Clean Air Devices | Periodic | 90 days | Work Order | Manufacturing / Quality Control
Biological Safety Cabinets | Periodic | 90 days | Work Order | Manufacturing / Quality Control
Classified Areas | Periodic | 60 days | Work Order | Manufacturing
Non-Classified Areas | Periodic | 90 days | Work Order | Manufacturing

## Slide 17
Areas / Types of inspections
Manufacturing
Quality Control
Labs
Warehouse
Utilities
Facilities / Rooms
Small Parts
Areas and Types of Inspections

## Slide 18: Equipment “At Use” Inspections
Adequate labeling/status tagging
Pre-use visual inspection - *Requires adequate light source confirmed upon inspection
Absence of leaks
Scope
System Critical Attributes
Criteria
Performed after pre-use CIP (batch to batch)
Performed by Manufacturing
Documented in Master Production Record

## Slide 19
Review latest monthly Overdue Work Order report. Identify and follow-up on open work orders related to findings from equipment inspection activities.
Perform Invasive Inspection checking original validated visual inspection locations (GMP Process Equipment)
Inspect EXTERNAL surfaces for rouge, staining or debris.
Inspect insulation for damage or disrepair.
Inspect piping penetrations through walls, ceilings and floors. Ensure finishes remain intact (e.g., caulking).
Ensure absence of leaks.
Verify equipment logbook adheres to closure and periodic review.
Ensure documentation adheres to Good Documentation Practices.
Inspect gearboxes, lifts, mechanical components for oil/fluid leaks.
Scope
Process Equipment & Skids, Utilities, Support Systems, Chambers, Hoods
Equipment/System Inspections
Criteria
Performed Quarterly except for Support Systems (monthly) and Process Equipment (variable)
Performed by Manufacturing
Driven by PM
Executed in CMMS

## Slide 20
Review latest monthly Overdue Work Order report per procedure. Identify and follow-up on open work orders related to findings from previous small parts inspection activities.
Inspect for rouge, scratches and damage per Small Parts Visual Inspection and Management procedure
Create Work Orders for all required follow-up inspections and remediation activities
Evaluate storage conditions of small parts in the area
Remove parts identified as ‘out of service’ from the area
Scope
Glasswasher and Autoclave Support Areas
Small Parts
Criteria
Performed quarterly
Performed by cross functional associate team
Driven by PM
Executed in CMMS

## Slide 21
Review latest monthly Overdue Work Order report per procedure. Identify and follow-up on open work orders related to findings from previous area inspection activities. Review Area Cleaning Logbooks to ensure adherence to cleaning procedure, including fixed vessel cleaning per procedure.
Room Finishes (Walls, Doors and Windows): Inspect for damaged paint (chipped/scratched/holes), cracks, missing or damaged caulking, damaged doors, windows, frames & hardware.
Room Finishes (Ceilings/Floors): Inspect for damaged paint (chipped/scratched/holes), cracks, missing or damaged caulking; damaged suspended ceiling trim and panels; sprinkler head escutcheons are sealed. Inspect floor drains for function and debris.
Transfer piping: Inspect for leaks, damaged or missing labels, loose hangers, insulation & escutcheons, and drain air gaps if required
Pest Control: Inspect for insects, ensure bug lights are operational, traps are in locations, as applicable. Ensure the Pest Control Activity Trending Report is reviewed per procedure
HVAC: Inspect return/supply grills/vents for cleanliness & blockage. Inspect duct insulation, for pooling condensation, AHU condition.
Electrical: Inspect switches, outlets, wiring, lighting fixtures (include caulk condition where applicable) to be in proper working condition. Inspect for items blocking panelboards.
Scope
Non-Classified and Classified Manufacturing Areas
Area Inspections
Criteria
Performed 60 days (Classified Space)
Performed Quarterly (Non-Classified Space)
Performed by Cross functional Associate Team
Driven by PM
Executed in CMMS

## Slide 22
Audit representative Equipment and Systems
Audit representative system logbooks and ensure they are within expiry and the review is current
Walls, Doors & Windows
Ceilings / Floors
Room Finishes
Pest Control
Piping
HVAC
Electrical
Scope
Inspect Classified and Non-Classified Area Boundary
Leadership Area GEMBA
Criteria
Classified and Non-classified
Performed every 6 months
Performed by Cross functional Leadership Team
Driven by PM
Executed in CMMS

## Slide 23
Work Orders should provide sufficient information to facilitate the continual improvement process and provide an accurate asset history. Governance activities such as trend analysis, review of overdue work, deviations, and performance reporting are examples where feedback from work execution process can be valuable to understand Fitness for Manufacturing
Trend maintenance activities as a means of achieving a higher level of asset performance
Establish control limits based on facility/equipment history along with age of asset
Establish periodic reporting to document and affirm fitness for manufacturing
Report elements may include:
    Corrective Work Order Trends
    Review of deviations related to critical failures/findings and decisions to continue manufacturing at risk
    Review Overdue PM Work
    Procedural summary – changes that could affect the FFM program and/or recommendations for improvement
    CAPAs/Pending Capital Work
    Follow-up actions/decisions
Governance and Oversight

## Slide 24
Apply resources to form a team to track end of life and reliability for equipment systems.
Reference ISPE Guide for Maintenance and Reliability.
Ensure procedures are in place for handling rouge / scratches / small parts.
Proactively determine work scheduling (Preventive Maintenance, Corrective Maintenance) and resource loading.
Utilize CMMS software and other systems to perform effective queries and tracking of progress.
Form and maintain partnerships between involved departments (Engineering, Facilities/Maintenance, Manufacturing, Quality, etc.)
Seek commitment from executive leadership.
Establish in-house capabilities for system maintenance / remediation (e.g., passivation) where feasible.
Recommendations & Lessons Learned